## S-Dew Point Flue Gas
Calculations for Recommended Flue Gas temperature to avoid S-dew point corrosion.
INPUTS
SO2 in flue gas ppm v/v |  |  | 80 | ppm v/v | as given by EMS Lab/Online analyser
FD Fan outlet air temperture |  |  | 30 | deg.c. | Site Reading
Flue gas pressure-Air preheater outlet |  |  | 15 | mm WC | Site Reading
H2O in flue gas |  |  | 5 | % vol | Lab analysis
CALCULATION(Please do not change the formulae)
SO2 in flue gas vol % |  | 0.008
H2O in flue gas vol % |  | 5
| Flue gas pressure | 15 | mm WC
|  | 0.59055 | inch WG
|  | 1.0015 | ata
[7 empty] | PH20 | 38.1104 | mm Hg
[7 empty] | Ln(PH2O) | 3.6405
[7 empty] | SO2 to SO3 | 2% | wt. basis
[7 empty] | PSO3 | 0.00097421 | mm Hg
[7 empty] | Ln(PSO3) | -6.9339
[7 empty] | 1000/Tdp | 2.6074
[7 empty] | Tdp | 383.525 | deg K
[8 empty] | 110.525 | Deg C
[7 empty] | tw recomm. | 110.525
[7 empty] | hi/(hi+ho) = | 0.4
[7 empty] | tI = | 30
[7 empty] | tw= | 110.525
[7 empty] | tg = | 164.2083
RESULTS
S-Dew Point Temperature |  |  | 110.525 | Deg.c.
Recommended Flue gas Temp |  |  | 164.2083 | Deg.c.
[6 empty] | Issued by | Technical Services
TCL Mithapur
18/04/2003
tw=tg-(tg-ti)xhi/(hi+ho) tw=average tube wall temperature tg,ti= flue gas and air inlet temperatures hi,ho= tube side and gas side heat transfer coefficients In an air preheater ,hi and ho=10 & 15 Btu/ft2hF respectively.
Dew Point of Acid Vapors Sulfurous acid 1000/Tdp=2.276-0.0294 ln(PH2O)-.0858 ln(PSO3)+0.0062 ln(PH2O)ln(PSO3) The dew points are in deg K and partial pressures in mm Hg.